| # ANFIS Method To Enhance FMEA Water Operation Model Of Indonesia Drinking Water Distribution System |  |
| --- | --- |

Diah Septiyana12 Mohamed Abd. Rahman2, Tasnim Firdaus Mohamed Ariff2, Nor Aiman Sukindar2, Erry Yulian T. Adesta3, Galang P. N. Hakim4*

1Department of Industrial Engineering, Faculty of Engineering, Universitas Muhammadiyah Tangerang, Banten, Indonesia.

2Department of Manufacturing and Material Engineering, Kulliyyah of Engineering (KOE), Kuala Lumpur,  International Islamic University Malaysia

3Department of Industrial Engineering Safety and Health, Faculty of Engineering, Universitas Indo Global Mandiri, Palembang, Indonesia.

4Department of Electrical Engineering, Universitas Mercu Buana, Jakarta 11650, Indonesia.

| Abstract In water operation, there are a lot of problems often found in the water treatment process and distribution. Those problems range from low to critical risk. To keep water treatment operation running all critical risk need to be address without delay. To identify the critical risk, the FMEA prioritize problem based on Occurrence, Severity, and Detection value. However, this method is also having problems. With the same RPN calculation thus, FMEA would ranking problem that have same RPN value, hence we have priority problem that not based on critical but based on highest value. to solve this problem, we propose additional method such as ANFIS to give weight based on risk level classification. From the results of data processing carried out by the ANFIS method, it is proven that it can perform re-ranking, for example in the L2, R5, S8, and U3 code which has an FMEA RPN value of 12. However, in FMEA-ANFIS the RPN value becomes L2 2.05, R5 1.52, S8 1.32, and U3 2.52. Furthermore, with these results, it can be concluded that the ANFIS method can enhance FMEA model in water operations. This is an open access article under the CC BY-SA license | Keywords: ANFIS; FMEA; Water Operation; Drinking Water; risk priority number . Article History: Received: May 2, 2019 Revised: May 29, 2019 Accepted: June 2, 2019 Published: June 2, 2019 Corresponding Author: Galang Persada nurani Hakim Electrical Engineering Department, Universitas Mercu Buana, Indonesia Email: galang.persada@mercubuana.ac.id |
| --- | --- |

INTRODUCTION

Clean water is the most important basic human life needs [1]. Excessive groundwater exploitation can cause a decline in environmental quality, such as salinization [2], aquifer depletion [3], and many others [4]. In the long term, this will cause a high economic cost for the community. To solve this problem, the Tangerang Regency Government has collaborated with a private drinking water company (concession) to provide clean water for the community in the Tangerang district area. In raw water treatment, many problems are often found in the water treatment process and distribution. The issues in the water distribution system include supply fulfillment, supply monitoring, network leaks, disruption of water supply, and pressure management. To solve this problem, quality improvement is needed, which the Tangerang Regency Government mandates in the Concession Agreement. Using Risk management can solve and enhance water distribution problems.

Various strategies are available for measuring risk levels and modeling risk techniques. Most approaches may be classified as either qualitative or quantitative, qualitative techniques attempt to describe risk in words or through categories, whereas quantitative methods convey risk numerically. The semi-quantitative is occasionally used to describe largely qualitative procedures, such as assigning a numerical value to probability and consequence classes. There are several methods in the risk assessment in water supply (qualitative, semi-qualitative or quantitative, deterministic or probabilistic, etc.), with the following tools (ETA, FTA, FMEA/FMECA, QMRA, HRA, Markov, etc) [5].

Failure Mode and Effects Analysis (FMEA) has been widely utilized to identify significant failure modes impacting the system and subsystems [6], [7].  FMEA is a quantitative method that a water company risk rating can represent. It exceeds various methods, given that it relies on a quantitative-proactive analysis of risk re-detection [8]. Historically, FMEA was established by the US military forces in the late 1940s [9]. The aerospace industry deployed it as a design process in the 1960s, with its inherent reliability and safety requirements [10]. Ford Motor Company introduced FMEA to the automobile industry in the late 1970s for safety and regulatory concerns [11]. The FMEA technique is widely utilized and recognized as a practical risk analysis and assessment tool for water operation [12]–[14], medic [15], [16], food [17], and others. The FMEA approach also has advantages such as enhancing the quality and reliability of the evaluated products and processes, determining the redesigning time of the product and lowering costs, reducing risks and their effects to a tolerable range and developing risk control plans, and providing information to eliminate primary risks enhance customer satisfaction [18].

Unfortunately, all FMEA methods have weaknesses. Even though the FMEA method was an exemplary method for finding failure in the system, it still has a problem, such as the risk that is different in severity has the same value because of the multiplication with occurrence and detection parameters [19]. According to Sharma et al., traditional FMEA approaches have limitations; in the CN calculation, the criticality number of the item may be underestimated when a failure mode has multiple effects in different severity categories since only the most severe effect is used in the calculation. In RPN analysis, various occurrence, severity, and detection sets may produce an identical value. However, the risk implication may differ, and the RPN ranking method has neglected the relative importance of occurrence, severity, and detection [20]. To solve this problem, Geramian [21] and Łapczyńska [22] propose to add a fuzzy method into FMEA. In this paper, ANFIS was proposed to solve the FMEA prioritize problem. ANFIS was enhanced by using neural network calculation so its value can automatically be readjusted in the input and output system[23].

METHOD

The research methodology can be see on figure 1.

Figure 1. The research step in this study.

In order to successfully enhance FMEA with ANFIS, we need to do the steps below:

- Identifying the production and quality control process.

- Identifying all potential failure modes of the production and quality control process, their effect on the production and quality control, and the cause of the failure modes.

- Assessing the system's failure modes for severity (S), occurrence (O), and detection (D).

- The FMEA then used to identify potential failure modes in the drinking water distribution process, determine their effect on product operation, occurrence and detection of current control when failures occur during the drinking water distribution process,

- Calculating the Risk Priority Number (RPN) to see the level of risk [29].

- Enhancing FMEA RPN using ANFIS Methods.

Failure Modes and Effect Analysis (FMEA)

It was first created as a formal design technique in the aerospace industry in the 1960s, and it has since become a decisive and vital factor for deterring potential issues and preventing their growth [25]. FMEA is one of the well-known quality management techniques used for continuous improvements in product or process designs. By ranking the priorities for corrective action according to the respective effects of the failures, the chance of the failures can be reduced or eliminated [26]. By definition, the FMEA becomes a systematic technique using engineering knowledge, reliability, and organizational development techniques or the method for optimizing the system, design, process, product, and service [27]. For each of the three parameters, a score of 1 to 5 (with one being the best and five being the worst scenario) and a risk-priority-number (RPN) are assigned. As a result, the RPN value aids the FMEA team in identifying the components that require immediate attention [28]. The mathematical model for FMEA would be:

RPN = O x S x D		(1)

Where:

O = the Occurrence value

S = the Severity value

D = the Detection value

FMEA RPN in Indonesia Water Operation

Data was gathered through risk identification based on interviews and observations of the drinking water distribution process. In this section, we interview three people with the most experience in water distribution, such as the manager and supervisor of the distribution department. Then, we examine direct statements using Standard Operating Procedure (SOP). Actual field conditions in the form of disturbances in the monitoring, supply, and water loss processes are used to determine risk effects. A risk assessment is performed based on the aspects identified during data collection. Table 1 presents the results of the Risk Priority Number (RPN) levels such as low, moderate, and critical.

Table 1 Calculation the RPN Value

| Failure Mode | Effect of Risk/Failure | Code | Cause of Risk/Failure | S | O | D | RPN | Risk Level |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Intermittent Water Pressure | Small water flow | L1 | Fluctuating Pressure | 4 | 4 | 3 | 48 | Critical |
|  |  | L2 | Production interruption | 4 | 1 | 3 | 12 | Low |
|  |  | L3 | Network quality is not worth it | 3 | 2 | 3 | 18 | Moderate |
|  |  | L4 | There is a leak in the pipe | 4 | 3 | 4 | 48 | Critical |
|  |  | L5 | External network disturbances, such as pipe leaks due to SDPU work | 3 | 2 | 3 | 18 | Moderate |
|  | Pressure/supply does not meet the demand | M1 | The valve cannot be operated | 4 | 3 | 3 | 36 | Moderate |
|  |  | M2 | Network quality is not proper | 4 | 3 | 4 | 48 | Critical |
|  |  | M3 | Inaccurate GIS data | 4 | 3 | 4 | 48 | Critical |
| Supply Fulfillment | Not achieving the target Pressure. | N1 | Lack of supply/pressure | 4 | 3 | 4 | 48 | Critical |
|  |  | N2 | The valve cannot be operated | 4 | 3 | 3 | 36 | Moderate |
|  |  | N3 | Network quality is not proper | 4 | 3 | 4 | 48 | Critical |
|  |  | N4 | There is a leak in the pipe | 4 | 3 | 4 | 48 | Critical |
| Supply Monitoring | The results of pressure monitoring do not match the conditions in the field | O1 | Measuring tools are not accurate | 3 | 2 | 3 | 18 | Moderate |
| Reduce water loss. | No water leak was found. | P1 | The network image does not match the pipe network in the field | 3 | 4 | 4 | 48 | Critical |
|  |  | P2 | Broken manometer | 3 | 3 | 2 | 18 | Moderate |
|  |  | P3 | Material Quality | 3 | 1 | 2 | 6 | Low |
|  |  | P4 | Changes in Water Pressure Increase | 3 | 2 | 3 | 18 | Moderate |
|  |  | P5 | Existence of external work (repair of waterways by SDPU, Telkom, PLN) | 3 | 4 | 3 | 36 | Moderate |
|  | Physical leaks do not rise to the ground | Q1 | Low Water Pressure | 4 | 4 | 3 | 48 | Critical |
|  |  | Q2 | Concrete Surface Type | 4 | 4 | 4 | 64 | Critical |
| Network leak repair | High Water Loss | R1 | Low quality of installed material | 3 | 3 | 3 | 27 | Moderate |
|  |  | R2 | House Connection Material Quality is low | 4 | 2 | 3 | 24 | Moderate |
|  |  | R3 | House Connection repair work quality is low | 4 | 2 | 3 | 24 | Moderate |
|  |  | R4 | The pipeline network is old | 5 | 2 | 4 | 40 | Moderate |
|  |  | R5 | Material availability | 3 | 2 | 2 | 12 | Low |
|  |  | R6 | Damaged supporting equipment (pump, generator, breaker) | 3 | 3 | 3 | 27 | Moderate |
|  |  | R7 | Lack of HR competence (3rd party) | 3 | 2 | 2 | 12 | Low |
|  | Water loss cannot be identified. | S1 | Customers do not get water at the time of isolation | 2 | 3 | 2 | 12 | Low |
|  |  | S2 | Change of pressure (zero pressure) | 2 | 3 | 3 | 18 | Moderate |
|  |  | S3 | Layered valve due to road elevation | 2 | 4 | 3 | 24 | Moderate |
|  |  | S4 | GIS data inaccuracies | 3 | 4 | 4 | 48 | Critical |
|  |  | S5 | The location of the Chamber, which is in the body or the middle of the road | 2 | 4 | 3 | 24 | Moderate |
|  |  | S6 | Disturbance of mass organization and Persons | 2 | 4 | 2 | 16 | Moderate |
|  |  | S7 | Lack of HR competence | 2 | 2 | 2 | 8 | Low |
|  |  | S8 | Lack of available human resources | 2 | 3 | 2 | 12 | Low |
|  | Not knowing physical or commercial water loss. | T1 | Rejection from customer | 2 | 3 | 2 | 12 | Low |
|  |  | T2 | Broken measuring instrument | 2 | 2 | 2 | 8 | Low |
|  |  | T3 | Battery run out | 2 | 2 | 2 | 8 | Low |
|  |  | T4 | Low measuring accuracy | 2 | 3 | 3 | 18 | Moderate |
|  |  | T5 | Disturbance of ORMAS and Persons | 2 | 4 | 2 | 16 | Moderate |
|  |  | T6 | Customer meter locations that are difficult to access | 4 | 4 | 2 | 32 | Moderate |
| District Meter/ Chamber Accessories Maintenance | Disruption of water supply | U1 | There is a blockage in the accessories | 2 | 4 | 2 | 16 | Moderate |
|  |  | U2 | Accessories age | 2 | 3 | 3 | 18 | Moderate |
|  |  | U3 | Valve Life | 2 | 2 | 3 | 12 | Low |
|  |  | U4 | Disturbance of ORMAS and Persons | 2 | 4 | 2 | 16 | Moderate |
| Pressure Management | Supply does not match demand. | V1 | Low-pressure inlet | 2 | 3 | 3 | 18 | Moderate |
|  |  | V2 | Tool durability | 2 | 3 | 3 | 18 | Moderate |
|  |  | V3 | Lack of HR competence | 2 | 3 | 2 | 12 | Low |
|  |  | V4 | Material availability | 3 | 2 | 2 | 12 | Low |
|  | Disrupted Pressure Management | W1 | Covid-19 Pandemic Conditions | 3 | 4 | 4 | 48 | Critical |

Table 1 show the results from field observations. we present the failure mode consequence and it cause. The failure mode in water operation especially in water supply consist of several part such as Intermittent Water Pressure, Supply Fulfillment, Supply Monitoring, Reduce water loss, Network leak repair, District Meter/ Chamber Accessories Maintenance, and Pressure Management. Each risk/failure effect can be caused by many things, so using those things the risks can be calculated. This calculation can be use in determine the severity, occurrence and detection rate based on Table 2. Using table 2 then we can calculated the RPN for each cause of risk/failure.

Table 2. Rating of Severity, Occurrence, and Detection [30]

| Rating | Severity | Occurrences | Detection |
| --- | --- | --- | --- |
| 1 | Very Low (VL) | Rare (R) | Almost Certain (AC) |
| 2 | Low (L) | Unlikely | Moderate (M) |
| 3 | Moderate (M) | Possible | Low (L) |
| 4 | High (H) | Likely | Very Low (VL) |
| 5 | Very High (VH) | Almost Certain | Absolute Uncertainty (AU) |

In table 2 the rating was consists of 5 level with each level contain separate linguistic variable. The risk assessment considers the impact of the risk's severity (severity level), the frequency of occurrence of the risk's cause (occurrence level), and whether the cause can be detected (detection level). The calculated RPN from table 1 and table 2 can be seen in table 3.

Table 3 Category for Risk Level from RPN Value (Risk type modify from[30]

| Color | Score | Risk Type | Criteria |
| --- | --- | --- | --- |
|  | 1-5 | Very Low (VL) | The risk that can cause a negligible amount of loss is called very low. |
|  | 6-15 | Low (L) | A risk that has a small potential for negative effects is called Low. |
|  | 16-40 | Moderate (M) | Risks that do not pose a major threat but significant losses can be classified as moderate. |
|  | 41-75 | Critical (C) | Risks that have a substantial negative effect and will seriously impact the success of a job are called critical. |
|  | >76 | Very Critical (VC) | Risk stemming from human or environmental error. Other causes can be procedural deficiencies or missing critical systems. This will require closure on the so-called catastrophic/very critical. |

The risk level scale is then determined using Table 3 after obtaining the Risk Priority Number (RPN) value. The risk level scale is divided into five categories: very low, low, medium, critical, and very critical. However, the results in Table 1 indicate that only three levels exist: low, moderate, and critical. To determine a scale of 1-5 for severity, occurrence, and detection. In Table 2, to simplify the rating, we modify from a 10 to a 5 rating in S, O, and D.

Adaptive Neuro-Fuzzy Inference System (ANFIS)

Zadeh developed the foundation of fuzzy in 1975 based on Linguistic Variables and their Application to Approximate Reasoning [31]. The fuzzy rule was subsequently created to model the qualitative elements of human knowledge (reasoning based on experience) and address the issue using those as its foundations [32]. Fuzzy is typically employed for control [33], including robot control [34], protection control [35]and many others. In 1985, Takagi and Sugeno created Fuzzy Sugeno [36]. A fuzzy Sugeno algorithm can be presented below :

Each output for step one is indicated by  , which is to increase the degree of membership.

O1i=µAixandO1i=µBix,i=1,2   (2)

Where:

i = each node of ANFIS architecture.

A, B= is the linguistic label.

x = is the input to node i. (such as small, large, etc.).

Every membership function type is usable at this stage. However, generalized bell types were employed to offer a maximum equal to 1 and a minimum equal to 0. Hence:

µAix=11 +x-ciai2bi                      (3)

Where:

a,b,c= is the parameter set.

The second step contributes to the firing strength of fuzzy inference by multiplying the two input signals. Each node represents this.

O2i=µAix.µBix,i=1,2            (4)

The following phase involved applying normalization for each fuzzy inference firing.

O3i= Wi=WiW1+W2 , i = 1, 2            (5)

Where:

W= is the firing strength of the node.

W = is the normalized firing strength of the node.

The following phase involved a calculation based on the parameters of the rule consequent in the following phase:

O4i=Wi.Fi= Wi.Pix+Qix+Rix,i=1,2   (6)

Where:

P, Q, R = is the parameter set.

The final phase computes the overall output by adding up all of the input signals:

Output=O5i=k=0nWi.Fi=k=1nWi .Fik=1nWi    (7)

Jang Jyh Shing Roger created the Adaptive Neuro-Fuzzy Inference System (ANFIS) in 1993  [23] based on fuzzy Takagi Sugeno's if-then rules. Based on its training data, the fuzzy inference system can adapt organically using the ANFIS approach. The Takagi-Sugeno fuzzy inference system is the foundation for the artificial neural network technique that makes up ANFIS [37]. This method can combine the benefits of fuzzy logic and neural networks into a single framework. A collection of fuzzy IF-THEN rules that can be learned to estimate nonlinear functions govern how this inference system operates. Consequently, ANFIS is regarded as a Universal Estimator (universal assessor). Equations 2 through 7 comprise the core algorithm used by ANFIS, which uses a fuzzy Sugeno algorithm. Jang then used gradient descent and chain rule to optimize its parameters. However, we must know the error rate for data training for each node output to do this since ANFIS learns through chain rule and gradient descent. The ANFIS architecture can be seen in Figure 5, and ANFIS algorithm can be seen from Equation 8 to Equation 13 :

If the data training sets have P numbers of inputs and the i-th position node outputs define Oi, then the error function may be calculated as follows:

Ep=m=1#L(Tmp- OLmp)2                 (8)

Where:

E= is the error measure, which is the sum of squared errors.

T = is the m component from the P output target vector.

O= is the m component from the actual output vector delivered by the P input vector.

Hence, the error rate can be calculated as:

∂Ep∂Oki p=m=1#k+1∂Ep∂Ok+1m p ∂Ok+1m p∂Oki p                 (9)

Where 1 ≤ k ≤ L-1 is the error rate of an internal node. It is expressed as the linear combination error rate of nodes in the next step. Therefore, for all 1 ≤ k ≤ L and 1 ≤ i ≤ #(k), we can find ∂Ep/(∂O k¦(i p)) using mathematical equations (8) and (9). Thus, we have α as a parameter of the adaptive network:

∂E∂α=o*∈S∂Ep∂O*∂O*∂α                    (10)

Where:

S= shows the set of nodes whose output depends on α.

Derivative for overall error measurement E concerning α is:

∂E∂α=p=1p∂Ep∂α                         (11)

Therefore, we can write the updated mathematical equations for generic parameter α as follows:

Δα = -η∂E∂α                          (12)

Where:

η = is a learning rate.

The learning rate can be written as:

η = kα (∂E∂α)2                          (13)

Where:

k= is the step size or length of each gradient transition in the parametric space.

RESULTS AND DISCUSSION

ANFIS FMEA RPN in Indonesia Water Operation

In this section, we would like to show Indonesia's new ANFIS FMEA risk model. In order to do that, we are training the ANFIS algorithm using data in Table 1. The new model will then be tested using risk evaluation to see the validity of our new model. Therefore, the fuzzification for the ANFIS FMEA RPN Indonesia Water Operation can be seen in Figure 2, Table 4, table 5, and equation 14 below:

(a)

(b)

(c)

Figure 2. ANFIS FMEA RPN Indonesia Water Operation. (a) fuzzification for severity, (b) for occurrence, and (c) for detection.

Table 4 Fuzzification of ANFIS FMEA RPN Indonesia Water Operation Model.

| No | Variable | Linguistic Variable | ANFIS FMEA Fuzzification |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | a | b | c |
| 1 | Severity | Low | 2.25 | 2.027 | 2.59 |
| 2 | Severity | High | 2.19 | 2.403 | 3.956 |
| 3 | Occurance | Low | 2 | 2.359 | 1.869 |
| 4 | Occurance | High | 2.16 | 1.95 | 3.506 |
| 5 | Detection | Low | 1.021 | 2.002 | 2.024 |
| 6 | Detection | High | 0.9888 | 1.997 | 4.017 |

In figure 2 and table 4 we present the fuzification for each RPN parameter such as figure 2a fuzzification for severity, figure 2b for occurrence, and figure 2c for detection. The fuzification are using 2 sets of linguistic variable such as “high” and “low” for each RPN parameter. The fuzification are also using generalized bell membership function types as in equation 3.

Table 5 Inference/rule of ANFIS FMEA RPN Indonesia Water Operation.

| Rule Index | Rule Firing | Rule Output | Fuzzy Constant Output |
| --- | --- | --- | --- |
| 1 | If input1 is Severity Low and input2 is Occurance Low and input3 is Detection Low | Then output1 is Very_Very_Low | -10.93 |
| 2 | If input1 is Severity Low and input2 is Occurance Low and input3 is Detection High | Then output1 is Very_Low | 18.82 |
| 3 | If input1 is Severity Low and input2 is Occurance High and input3 is Detection Low | Then output1 is Low | 7.487 |
| 4 | If input1 is Severity Low and input2 is Occurance High and input3 is Detection High | Then output1 is Moderate | -7.164 |
| 5 | If input1 is Severity High and input2 is Occurance Low and input3 is Detection Low | Then output1 is High | 7.683 |
| 6 | If input1 is Severity High and input2 is Occurance Low and input3 is Detection High | Then output1 is Higher | -10.3 |
| 7 | If input1 is Severity High and input2 is Occurance High and input3 is Detection Low | Then output1 is Critical | 2.89 |
| 8 | If input1 is Severity High and input2 is Occurance High and input3 is Detection High | Then output1 is Very_Critical | 15.34 |

Because the fuzzy was developed from linguistic variables and its practice of approximate reasoning [32]. With that foundation, we can conclude that fuzzy, in this case ANFIS where the fuzzy rule, was developed in order to describe the qualitative aspects of human expertise (the reasoning based on experience) [38] to solve the problem [39].  In conclusion, the fuzzy model was based on fuzzy rule reasoning for solving problems. Therefore, we can see that the fuzzy ANFIS rule was in general form and can be used to enhance FMEA RPN Indonesia Water Operation. In table 5 The fuzzy rule was created automatically depend on linguistic variable sets amount, while the Fuzzy Constant Output are generated automatically based on neural network backpropagation calculation method.

Then, using equation 3 and equation 7, we can develop the mathematical model for the ANFIS FMEA RPN Indonesia Water Operation. The proposed model can be seen in equation 14 below:

Bi= k=0n11 +x-ciai2bi+11 +x-ciai2bi FAPk=0n11 +x-ciai2bi+11 +x-ciai2bi        (14)

Where:

x = Describe input parameters such as Severity, occurrence, and Detection.

ai = Describe the broadness of membership function input, including severity, occurrence, and detection.

bi = Describe the form of the curve on either side of the middle of Severity, Occurrence, Detection.

ci= Describe the center of the membership function of Severity, Occurrence, and Detection.

FAP= Fuzzy constant output based on the parameters of the rule consequent.

n= ANFIS Inference/Rule firing Strength index.

Bi= output such as weight of FMEA.

ANFIS FMEA RPN Indonesia Water Operation

By using Table 1 and the ANFIS model, Equation 13 so that it can be measured the Risk Priority Number using the ANFIS fitting model in Table 6 below:

Table 6 RPN FMEA-ANFIS versus RPN FMEA Conventional

| Code | Cause of Risk/Failure | S | O | D | RPN FMEA | RPN FMEA-ANFIS | Risk Level |
| --- | --- | --- | --- | --- | --- | --- | --- |
| L2 | Production interruption | 4 | 1 | 3 | 12 | 2.05 | Low |
| R5 | Material availability | 3 | 2 | 2 | 12 | 1.52 | Low |
| S8 | Lack of available human resources | 2 | 3 | 2 | 12 | 1.32 | Low |
| U3 | Valve Life | 2 | 2 | 3 | 12 | 2.52 | Low |
| P2 | Broken manometer | 3 | 3 | 2 | 18 | 1.98 | Moderate |
| P4 | Changes in Water Pressure Increase | 3 | 2 | 3 | 18 | 2.69 | Moderate |
| S2 | Change of pressure (zero pressure) | 2 | 3 | 3 | 18 | 2.68 | Moderate |
| T4 | Low measuring accuracy | 2 | 3 | 3 | 18 | 1.32 | Moderate |
| R3 | House Connection repair work quality is low | 4 | 2 | 3 | 24 | 2.75 | Moderate |
| S5 | The location of the Chamber, which is in the body or the middle of the road | 2 | 4 | 3 | 24 | 3.1 | Moderate |
| R1 | Low quality of installed material | 3 | 3 | 3 | 27 | 2.94 | Moderate |
| T6 | Customer meter locations that are difficult to access | 4 | 4 | 2 | 32 | 3.29 | Moderate |
| M1 | The valve cannot be operated | 4 | 3 | 3 | 36 | 3.03 | Moderate |
| P5 | Existence of external work (repair of waterways by SDPU, Telkom, PLN) | 3 | 4 | 3 | 36 | 3.59 | Moderate |
| R4 | The pipeline network is old | 5 | 2 | 4 | 40 | 3.00 | Moderate |
| L1 | Fluctuating Pressure | 4 | 4 | 3 | 48 | 3.77 | Critical |
| N1 | Lack of supply/pressure | 4 | 3 | 4 | 48 | 3.96 | Critical |
| P1 | The network image does not match the pipe network in the field | 3 | 4 | 4 | 48 | 4.05 | Critical |
| Q1 | Low Water Pressure | 4 | 4 | 3 | 48 | 3.77 | Critical |
| S4 | GIS data inaccuracies | 3 | 4 | 4 | 48 | 4.05 | Critical |
| Q2 | Concrete Surface Type | 4 | 4 | 4 | 64 | 4.31 | Critical |

Table 6 above selects the same RPN FMEA value and then reduces it to compare RPN FMEA and RPN FMEA-ANFIS. From the results of the table above, it can be seen that the ANFIS algorithm improves the RPN FMEA value. As an example, it can be seen that L2, R5, S8, and U3 have an RPN FMEA value of 12, but in FMEA-ANFIS, the RPN value becomes L2 2.05, R5 1.52, S8 1.32 and U3 2.52. So the priority order of the "low" risk level in Table 5 becomes U3(1), L2(2), R5(3), and S8(4). Another example can be seen at the "critical" risk level where the code L1, N1, P1, Q1, S4, Q2 with an RPN FMEA value of 48, but using the ANFIS model, the RPN FMEA-ANFIS value becomes L1 3.77, N1 3.96, P1 4.05, Q1 3.77, S4 4.05, and Q2 4.31. So the priority order of the "Critical" risk level in Table 5 becomes Q2 (1), S4 (2), P1(3), N1(4) and L1(5), Q1(6). Although ANFIS can help improve RPN FMEA values, not all can be corrected. With the example in code P1 and S4 where the total RPN value has the same value and also the Severity (S), Occurrence (O), and Detection (D) parameter values are the same so that the RPN FMEA value has the same value too, with this then the RPN FMEA-ANFIS model will produce the same value.

CONCLUSION

In this paper, we propose to improve the RPN FMEA value using the ANFIS method. The data processing results by the ANFIS method prove that it can perform re-prioritization, for example, in the L2, R5, S8, and U3 code, which has an FMEA RPN value of 12. However, the RPN FMEA-ANFIS value becomes L2 2.05, R5 1.52, S8 1.32, and U3 2.52. Thus, with these results, it can be concluded that the ANFIS method can enhance the FMEA model in water operations.

ACKNOWLEDGMENT

This research is supported by Hibah Riset Nasional Muhammadiyah Batch VII Tahun 2024 Nomor: 0258.106/I.3/D/2024.

REFERENCES

[1]	E. Kurniati, Kamariah, and T. Susilawati, “Analysis of clean water distribution systems using EPANET 2.0 (Case study of Uma Sima Village, Sumbawa Regency),” in IOP Conference Series: Earth and Environmental Science 708, 2021, doi: 10.1088/1755-1315/708/1/012105.

[2]	F. Dong, Y. Tang, X. Xing, Z. Liu, and L. Xing, “Formation and evolution of soil salinization in Shouguang city based on PMS and OLI/TM sensors,” Water (Switzerland), vol. 11, no. 2, p. 345, 2019, doi: 10.3390/w11020345.

[3]	A. G. Prayag, Y. Zhou, V. Srinivasan, T. Stigter, and A. Verzijl, “Assessing the impact of groundwater abstractions on aquifer depletion in the Cauvery Delta, India,” Agric. Water Manag., vol. 279, 2023, doi: 10.1016/j.agwat.2023.108191.

[4]	Z. Zhang, C. Xiao, W. Yang, O. A. Adeyeye, and X. Liang, “Effects of the natural environment and human activities on iron and manganese content in groundwater: a case study of Changchun city, Northeast China,” Environ. Sci. Pollut. Res., vol. 28, pp. 41109–41119, 2021, doi: 10.1007/s11356-021-13576-4.

[5]	G. O. M. Kombo Mpindou, I. Escuder Bueno, and E. Chordà Ramón, “Risk analysis methods of water supply systems: comprehensive review from source to tap,” Appl. Water Sci., vol. 12, no. 56, 2022, doi: 10.1007/s13201-022-01586-7.

[6]	H. Li, M. Liang, F. Li, J. Zuo, C. Zhang, and Y. Ma, “Operational safety risk assessment of water diversion infrastructure based on FMEA with fuzzy inference system,” Water Supply, vol. 22, no. 10, pp. 7513–7531, 2022, doi: 10.2166/ws.2022.322.

[7]	D. Septiyana, “FUZZY FMEA Application To Identification Risk In-Process Production Of Toyota Hi-Ace Wiring Harness Product,” J@ti Undip J. Tek. Ind., vol. 16, no. 3, pp. 153–160, 2021, doi: 10.14710/jati.16.3.153-160.

[8]	N. G. Mutlu and S. Altuntas, “Risk analysis for occupational safety and health in the textile industry: Integration of FMEA, FTA, and BIFPET methods,” Int. J. Ind. Ergon., vol. 72, pp. 222–240, 2019, doi: 10.1016/j.ergon.2019.05.013.

[9]	I. Nicolin and B. A. Nicolin, “Failure Mode and Effect Analysis for a military nose landing gear project,” INCAS Bull., vol. 13, no. 4, p. 205, 2021, doi: 10.13111/2066-8201.2021.13.4.17.

[10]	V. Salma, F. Friedl, and R. Schmehl, “Improving reliability and safety of airborne wind energy systems,” Wind Energy, vol. 23, no. 2, pp. 340–356, 2020, doi: 10.1002/we.2433.

[11]	H. Amrutha, J. Ajinkya, and M. Surabhi, “Application of failure modes and effects analysis (FMEA) in automated spot welding process of an automobile industry: A case study,” J. Eng. Educ. Transform., vol. 34, pp. 281–289, 2020, doi: 10.16920/jeet/2021/v34i0/157156.

[12]	H. Haider, M. H. Alkhowaiter, M. D. Shafiquzzaman, M. Alresheedi, S. S. AlSaleem, and A. R. Ghumman, “Source to Tap Risk Assessment for Intermittent Water Supply Systems in Arid Regions: An Integrated FTA—Fuzzy FMEA Methodology,” Environ. Manage., vol. 67, pp. 324–341, 2021, doi: 10.1007/s00267-020-01400-7.

[13]	A. Wicaksono and N. Karnaningroem, “Minimizing failure risk of refill drinking water production in Rungkut district Surabaya using Failure Mode and Effect Analysis (FMEA),” in IOP Conference Series: Earth and Environmental Science259, 2019, doi: 10.1088/1755-1315/259/1/012013.

[14]	M. Caithamlová, Š. Kročová, and J. Mariňáková, “Operation of Water Supply Systems in the Czech Republic—Risk Analysis,” Appl. Sci., vol. 14, no. 4, p. 1572, 2024, doi: 10.3390/app14041572.

[15]	M. L. Chiozza and C. Ponzetti, “FMEA: A model for reducing medical errors,” Clin. Chim. Acta, 2009, doi: 10.1016/j.cca.2009.03.015.

[16]	“Evaluating the application of failure mode and effects analysis technique in hospital wards: a systematic review,” J. Inj. Violence Res., 2017, doi: 10.5249/jivr.v9i1.794.

[17]	A. Szczyrba and S. Dziuba, “Good Manufacturing Practices for Quality and Safety Management in the Food Industry,” in Materials Research Proceedings 34, 2023, pp. 288–297, doi: 10.21741/9781644902691-34.

[18]	N. Nurwahyudi and E. Rimawan, “Analysis of customer satisfaction in freight forwarder industry using servqual, ipa and fmea methods,” Sci. J. Marit. Res., vol. 35, pp. 109–117, 2021, doi: 10.31217/p.35.1.12.

[19]	M. Yucesan, M. Gul, and E. Celik, “A holistic FMEA approach by fuzzy-based Bayesian network and best–worst method,” Complex Intell. Syst., vol. 7, pp. 1547–1564, 2021, doi: 10.1007/s40747-021-00279-z.

[20]	R. K. Sharma, D. Kumar, and P. Kumar, “Systematic failure mode effect analysis (FMEA) using fuzzy linguistic modelling,” Int. J. Qual. Reliab. Manag., vol. 22, no. 9, pp. 986–1004, 2005, doi: 10.1108/02656710510625248.

[21]	A. Geramian, A. Abraham, and M. Ahmadi Nozari, “Fuzzy logic-based FMEA robust design: a quantitative approach for robustness against groupthink in group/team decision-making,” Int. J. Prod. Res., vol. 57, no. 5, pp. 1331–1344, 2019, doi: 10.1080/00207543.2018.1471236.

[22]	D. Łapczyńska and A. Burduk, “Fuzzy FMEA Application to Risk Assessment of Quality Control Process,” in Advances in Intelligent Systems and Computing 1268, 2021, doi: 10.1007/978-3-030-57802-2_30.

[23]	J. S. R. Jang, “ANFIS: Adaptive-Network-Based Fuzzy Inference System,” IEEE Trans. Syst. Man Cybern., vol. 23, no. 3, pp. 665–685, 1993, doi: 10.1109/21.256541.

[24]	J. Ivančan and D. Lisjak, “New fmea risks ranking approach utilizing four fuzzy logic systems,” Machines, vol. 9, no. 11, p. 292, 2021, doi: 10.3390/machines9110292.

[25]	M. Sagnak, Y. Kazancoglu, Y. D. Ozkan Ozen, and J. A. Garza-Reyes, “Decision-making for risk evaluation: integration of prospect theory with failure modes and effects analysis (FMEA),” Int. J. Qual. Reliab. Manag., vol. 37, no. 6/7, pp. 939–956, 2020, doi: 10.1108/IJQRM-01-2020-0013.

[26]	Z. Wu, W. Liu, and W. Nie, “Literature review and prospect of the development and application of FMEA in manufacturing industry,” Int. J. Adv. Manuf. Technol., vol. 112, pp. 1409–1436, 2021, doi: 10.1007/s00170-020-06425-0.

[27]	D. H. Stamatis, Failure Mode and Effect Analysis: FMEA from Theory to Execution. Germany: ASQ Quality Press, 2003.

[28]	H. C. Liu, X. Q. Chen, C. Y. Duan, and Y. M. Wang, “Failure mode and effect analysis using multi-criteria decision making methods: A systematic literature review,” Comput. Ind. Eng., vol. 135, pp. 881–897, 2019, doi: 10.1016/j.cie.2019.06.055.

[29]	M. Kumru and P. Y. Kumru, “Fuzzy FMEA application to improve purchasing process in a public hospital,” Appl. Soft Comput. J., vol. 13, no. 1, pp. 721–733, 2013, doi: 10.1016/j.asoc.2012.08.007.

[30]	Y. M. Wang, K. S. Chin, G. K. K. Poon, and J. B. Yang, “Risk evaluation in failure mode and effects analysis using fuzzy weighted geometric mean,” Expert Syst. Appl., vol. 36, no. 2 PART 1, pp. 1195–1207, 2009, doi: 10.1016/j.eswa.2007.11.028.

[31]	L. A. Zadeh, “Fuzzy Sets,” Inf. Control, vol. 8, no. 3, pp. 338–353, 1965.

[32]	L. A. Zadeh, “The Concept of a Linguistic Variable and its Application to Approximate Reasoning,” Inf. Sci. (Ny)., vol. 8, no. 3, pp. 199–249, 1975.

[33]	S. R. Utama, A. Firdausi, and G. P. N. Hakim, “Control and Monitoring Automatic Floodgate Based on NodeMCU and IOT with Fuzzy Logic Testing,” J. Robot. Control, vol. 3, no. 1, pp. 14–17, 2022, doi: 10.18196/jrc.v3i1.11199.

[34]	A. Adriansyah, E. Ihsanto, C. Anam, S. Indriyanto, A. Baihaqi, and J. Andika, “Autonomous Mobile Robot Design with Behaviour-based Control Architecture using Adaptive Neuro-Fuzzy Inference System (ANFIS),” in 2022 FORTEI-International Conference on Electrical Engineering, FORTEI-ICEE 2022 - Proceeding, 2022, doi: 10.1109/FORTEI-ICEE57243.2022.9972931.

[35]	A. S. Rizal, A. Adriansyah, S. Budiyanto, S. C. Haryanti, and U. A. Rachmawati, “Overcurrent relay coordination using an adaptive neuro fuzzy inference systems (ANFIS),” EEA - Electroteh. Electron. Autom., vol. 68, no. 3, pp. 55–62, 2020, doi: 10.46904/eea.20.68.3.1108007.

[36]	T. Tagaki and M. Sugeno, “Fuzzy Identification of System and its Application to Modeling and Control,” IEEE Trans. Syst. Man Cybern., vol. 15, no. 1, pp. 116–132, 1985.

[37]	J.-S. R. Jang, C.-T. Sun, and E. Mizutani, Neuro-Fuzzy and Soft Computing-A Computational Approach to Learning and Machine Intelligence. Prentice Hall, 1997.

[38]	N. Yusof, N. Bahiah, M. Shahizan, and Y. Chun, “A Concise Fuzzy Rule Base to Reason Student Performance Based on Rough-Fuzzy Approach,” in Fuzzy Inference System - Theory and Applications, 2012.

[39]	C. U. Yeom and K. C. Kwak, “Adaptive neuro‐fuzzy inference system predictor with an incremental tree structure based on a context‐based fuzzy clustering approach,” Appl. Sci., vol. 10, no. 23, p. 8495, 2020, doi: 10.3390/app10238495.